Study of Some Chemical Characteristics and Total Count of E coli form  Bacteria in  Drinking Water Plants in Ilaje Jboor

Region –Hilla

Batool Mohamed Hassan Al-Adily

College of science – University of Babylon

Abstract

This study deals with measuring of some  chemical parameters including :pH, EC,  SO4-2, Cl -,Ca+2, total hardness, and alkalinity of drinking water in Ilaje Jboor in Hilla governet  . The total count of coli form  bacteria was also studied, to evaluate the quality of drinking water.

During the period  from April  2008 to February 2009  samples ware collected monthly. The analysis explained that drinking water depending on characters of  raw water (river) and the efficiency of drinking water plants different but in most samples the chemical parameters were within compared  EPA,WHO and Iraqi guidelines of drinking water.The results indicated  that the  water which was processed in Ilaje Jboor can not be used for drinking  because of contamination of E. coli form  bacteria.

الخلاصة

تضمنت هذه الدراسة قياس عدد من الخواص الكيميائية متمثلة بالاس الهيدروجيني والتوصيلية الكهربائية و تراكيز الكالسيوم، المغنيسيوم، الكلوريدات، الكبريتات، العسرة الكلية، والقاعدية في ماء الشرب في منطقة علاج جبور في مدينة الحلة. كما شملت دراسة العدد الكلي لبكتريا القولون لغرض تحديد نوعية ماء الشرب.

خلال المدة بين نيسان 2008 وحتى نهاية شباط 2009 تم جمع العينات شهرياً. اوضحت نتائج تحليل العينات بأن خواص مياه الشرب تعتمد على خواص الماء الخام (النهر) وان كفاءة محطات مياه الشرب متباينة من ناحية الصفات الكيميائية والفيزيائية قيد الدراسة في معظم العينات اذ كانت ضمن محددات EPA  و WHO والمحددات العراقية لمياه الشرب.غير ان تلوث المياه ببكتريا القولون يجعله غير ملائم للشرب.

Introduction

Water is essential to life and satisfactory supply must be available to all. Improving access to safe drinking water can result in tangibles to health(HNMRC,2004).

Health concerns associated with chemical constituents of drinking water differ from those associated with microbial contamination ,some chemical found normal in water but when increase than normal levels lead to health problem(WHO,2004),for example drinking water must have amount of sulfate less than 250 ppm but when increase more this concentration caused thickness of intestine and laxative(WHO,1996). While increase nitrate more 10 ppm caused methemoglobinemia(office of environment health,2005). The microbiological quality of drinking water is the most important aspect  of drinking water because of its association with waterborne diseases as well as typhoid fever and choleraOnteria,2006),and the hourly toll from biological contamination of  drinking water is 400 deaths of children(Askork,1998).

To protect the health, water must be treated before used for drinking  and first document drinking water treatment can be found in Egyptian hieroglyphic describing procedures to purify water by boiling ,filtration and chemical treatment (Michalski,2005).The drinking water system must have and continuously maintain robust multiple barriers appropriate to the level of potential contamination facing the water supply (Nitm,2004).

Many studies explained that  drinking water systems in Hilla city are not efficient  to reduced bacterial contamination due to bad precipitation ,and bad sedimentation processes (Al Azawi,1998&Al Azawi,2004).

Experimental part

The samples were collected from 6 positions from three drinking water plants as well as show in figure (1).The positions 1,3 and5 were collected from river which used as raw water to supply these plants ,wile 2,4and 6 positions were from houses nearest to plants . From April  2008 to February 2009 samples were collected monthly from Ilaje Jboor Region which lies on the way from Hilla to Diwaniyah about 10 km east Hilla city center. Population in  this region were using river water for all uses but in 2007 a small drinking water plants build up, and this study come to evaluate water that produced by these plants.

Euphrates

Hilla

Hilla River

1

a

2

b

3

4

5

C

6

Figure  1:a diagram explain positions of samples

Scale 1/600000

a     Drinking water plant

b     Drinking water plant

c     Drinking water plant

The standard methods for drinking water analysis(WHO,200) were used to determine concentrations of calcium and total hardness, while alkalinity ,chloride ,sulfate, phosphate were determined according to A.P.H.A. methods(APHA,1975).Parsons method used to evaluate nitrate concentrations(Parsons et al,1984),and depended  a classic method to analysis total count of bacteria(Al Moffraji et al,1991).

Results and Discussion

Table 1 show the chemical parameters which studied in water of samples in sex positions.

Table 1 chemical characteristics of water in sample

| Parameters | Date position | Ap\ 2008 | Ma\ 2008 | Ju\ 2008 | jul\ 2008 | Oct\ 2008 | Sp\ 2008 | Oc\ 2008 | No\ 2008 | De\ 2008 | Ja\ 2009 | Fa/ 2009 | Range |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 1 | 6.7 | 7.2 | 7.2 | 7.8 | 6.9 | 7.6 | 6.8 | 6.9 | 7 | 7.5 | 7.3 | 6.7-7.8 |
|  | 2 | 6.8 | 7.1 | 7.1 | 7.3 | 6.9 | 7.7 | 6.8 | 6.8 | 6.9 | 7.5 | 7.3 | 6.8-7.7 |
|  | 3 | 7.4 | 7 | 7.3 | 7.3 | 6.8 | 7.6 | 6.8 | 6.95 | 7.1 | 7.45 | 7.45 | 6.8-7.45 |
|  | 4 | 7.5 | 7.3 | 7.4 | 7.1 | 6.6 | 7.6 | 6.8 | 6.75 | 7.1 | 7.3 | 7.5 | 6.6-7.5 |
|  | 5 | 7.5 | 7.3 | 7.3 | 7.3 | 7.2 | 7.2 | 6.9 | 7.1 | 7.1 | 7.45 | 7.5 | 6.9-7.5 |
|  | 6 | 7.4 | 7.2 | 7.3 | 7.3 | 7 | 7.2 | 6.8 | 6.8 | 6.9 | 7.5 | 7.5 | 6.8-7.5 |
| EC (micro mohs) | 1 | 1034 | 1048 | 808 | 923 | 970 | 842 | 839 | 967 | 770 | 845 | 810 | 770-1048 |
|  | 2 | 1045 | 980 | 793 | 948 | 992 | 875 | 822 | 955 | 763 | 841 | 783 | 763-1045 |
|  | 3 | 1017 | 953 | 785 | 941 | 1000 | 878 | 830 | 958 | 771 | 813 | 778 | 771-1017 |
|  | 4 | 1041 | 965 | 813 | 991 | 988 | 866 | 821 | 974 | 773 | 825 | 778 | 773-1041 |
|  | 5 | 1051 | 882 | 797 | 921 | 984 | 875 | 794 | 973 | 773 | 818 | 804 | 773-1051 |
|  | 6 | 1050 | 955 | 759 | 982 | 980 | 897 | 832 | 1028 | 791 | 808 | 778 | 759-1050 |
| Alkalinity (ppm) | 1 | 200 | 100 | 180 | 40 | 40 | 60 | 5 | 90 | 135 | 180 | 120 | 50-200 |
|  | 2 | 200 | 120 | 140 | 40 | 50 | 60 | 30 | 80 | 125 | 120 | 100 | 30-200 |
|  | 3 | 300 | 100 | 100 | 30 | 50 | 80 | 60 | 95 | 100 | 165 | 140 | 30-300 |
|  | 4 | 150 | 120 | 120 | 50 | 50 | 70 | 60 | 95 | 115 | 165 | 140 | 50-165 |
|  | 5 | 150 | 100 | 140 | 50 | 40 | 90 | 100 | 115 | 120 | 155 | 15 | 40-155 |
|  | 6 | 150 | 120 | 120 | 40 | 50 | 80 | 50 | 111 | 160 | 125 | 130 | 40-150 |
| Cl- (ppm) | 1 | 581 | 664 | 611 | 508 | 334 | 218 | 262 | 78 | 189 | 209 | 199 | 78-664 |
|  | 2 | 508 | 436 | 348 | 654 | 320 | 276 | 233 | 63 | 231 | 219 | 189 | 63-654 |
|  | 3 | 654 | 436 | 494 | 509 | 305 | 349 | 189 | 59 | 184 | 209 | 147 | 59-654 |
|  | 4 | 581 | 291 | 291 | 582 | 334 | 305 | 320 | 49 | 186 | 206 | 284 | 49-582 |
|  | 5 | 127 | 436 | 611 | 473 | 334 | 349 | 305 | 74 | 201 | 209 | 216 | 74-473 |
|  | 6 | 654 | 407 | 785 | 727 | 378 | 262 | 323 | 66 | 171 | 284 | 264 | 66-785 |
| T H (ppm) | 1 | 260 | 560 | 200 | 160 | 70 | 100 | 100 | 380 | 370 | 460 | 300 | 70-560 |
|  | 2 | 230 | 580 | 140 | 140 | 130 | 110 | 100 | 370 | 420 | 470 | 460 | 100-580 |
|  | 3 | 290 | 560 | 100 | 120 | 110 | 110 | 110 | 420 | 420 | 355 | 330 | 100-560 |
|  | 4 | 370 | 640 | 180 | 140 | 130 | 140 | 110 | 515 | 515 | 315 | 410 | 110-640 |
|  | 5 | 320 | 480 | 180 | 90 | 100 | 120 | 120 | 450 | 450 | 295 | 380 | 90-480 |
|  | 6 | 320 | 720 | 220 | 50 | 80 | 140 | 160 | 410 | 410 | 340 | 350 | 50-720 |
| Ca+2 (ppm) | 1 | 60.2 | 160.3 | 200.4 | 100.2 | 20.01 | 80.2 | 40.1 | 78 | 162 | 184 | 80 | 20.01-184 |
|  | 2 | 60.2 | 80.1 | 80.2 | 60.1 | 40.1 | 60.1 | 60.1 | 50 | 154 | 80 | 72 | 100-580 |
|  | 3 | 80.1 | 140.3 | 80.2 | 40.1 | 40.1 | 70.1 | 60.1 | 64 | 96 | 66 | 52 | 100-560 |
|  | 4 | 60.1 | 120.2 | 60.1 | 40.1 | 30.1 | 30.1 | 80.2 | 44 | 96 | 116 | 190 | 110-640 |
|  | 5 | 60.1 | 80.2 | 60.1 | 80.2 | 20.04 | 40.1 | 100.2 | 28 | 90 | 120 | 68 | 90-480 |
|  | 6 | 60.1 | 60.1 | 40 | 20.04 | 20.04 | 20.1 | 50.1 | 28 | 96 | 82 | 70 | 50-720 |
| So4-2 (ppm) | 1 | 166 | 329 | 93 | 80 | 72 | 89 | 204 | 139 | 341 | 291 | 402 | 20.01-184 |
|  | 2 | 158 | 90 | 223 | 179 | 150 | 211 | 221 | 95 | 147 | 229 | 365 | 50-154 |
|  | 3 | 157 | 267 | 232 | 157 | 168 | 184 | 222 | 193 | 87 | 397 | 392 | 40.1-140-3 |
|  | 4 | 189 | 139 | 210 | 105 | 113 | 181 | 207 | 164 | 130 | 397 | 285 | 30.1-120.2 |
|  | 5 | 159 | 159 | 222 | 128 | 170 | 151 | 219 | 150 | 107 | 420 | 374 | 28-120 |
|  | 6 | 168 | 173 | 205 | 90 | 99 | 188 | 225 | 85 | 161 | 909 | 317 | 20.04-96 |

The pH values ranged 7.8-6.6 which are within the  normal values as show in table 2 which summarized the guidelines of drinking water (WHO,2006,EPA,1999 and Iraqi Standards,1976) .

Drinking water plants not effecting on pH due to their processing which depending on chlorination and lime addition in some days.

Alkalinity concentration were differencing from month to month ,high values were recorded in March while lower values were in July , August  , September, and December. The decrease of alkalinity values due to increase in temperature which made carbonate and bicarbonate break up to carbon dioxide(Taj aldeen,2003).                       Study classified two types of water according to the total hardness concentration. First was very hard water which were above 180 ppm ((Al Moffraji et al,1991) these concentrations can seen in samples of March , April , December, January, and February. Second type of water was hared which seen in other months ranged 50-160 ppm . Increase and decrease of TH values depending on rate of irrigation  which effected on dissolving of  bicarbonate from soil that at end inter the river (Taj aldeen,2003).

High concentration of total hardness in drinking water (above 500 ppm) have negative effect on health by causing many diseases  associated with kidney (Davison,1999).

Calcium as show in table 2 were not different from TH . Ca+2 concentration difference from month to another and ranged 20.04-200.8 ppm which are normal values .Plants didn’t effect on Ca+2 concentration which depending on         concentration in river.

This study explained very high levels of chlorides in river and drinking water. Concentrations ware above maximum contaminant level ( M C L) of chloride which about 200 ppm(Iraqi Standards,1976) ;except samples of November and December and samples of 1,2 and 3 positions  in January that ranged 49-199 ppm as well as explained in table 2 .Cl increased in spring , summer and autumn mater due to evaporation of water and concentration of water by heat in these seasons.

Sulfate were various through period of study in river water . Lower values recorded in hot month contrast with samples that collected in winter mater lead to think that almost sulfate resources are natural which increase in water by raining . Sulfate in drinking water ware differ from plant to another and where differ from sample to sample in same plant .Plants produced water with high concentrations of sulfate in some times (specially in plant 1) because of additions of alum as coagulant agent to reduce turbidity of water; whoever that almost sulfate concentrations were within guideline of drinking water which about 500 ppm as sodium sulfate (WHO,2000).

The electrical conductivity(EC) values were differencing as the values of anions and cations and pH values. EC ranged 763-1051micro mohs, these values more than medium of lower values that recorded in drinking water of Hilla city in another study which was about 540 micro mohs((Al Azawi,1998).

Table 2 some characteristics of drinking water

| Parameter |  | Unit | WHO Guideline (WHO,2006) | US EPA Guideline (EPA,1999) | Iraqi guideline ( Iraqi Standards, 1976) |
| --- | --- | --- | --- | --- | --- |
| pH |  | -- | 6.5-8.5 | 6.5-8.5 | 6.5-8.5 |
| TDS |  | Micromohs | 1000 | 500 | -- |
| EC |  | PPM | 1600 | 755 | -- |
| Mg |  | PPM | -- | -- | 50 |
| Ca |  | PPM | -- | -- | 200 |
| T H |  | PPM | 500 | -- | 500 |
| Na |  | PPM | 200 | -- | -- |
| So4 |  | PPM | 400 | 250 | 200 |
| Total count of bacteria | Cell/100 ml of sample |  | 0.0 | 0.0 | 5 |

Table 3 explained the total count of coli form bacteria. River water was contaminated with coli form bacteria . Plants were reducing total count of bacteria (but not preventing it) by chlorination.

Table 3 total count of bacteria cell /100 ml

| Range | Fa/ 2009 | Jan/2009 | De/2008 | NO/2008 | OC/2008 | SP/2008 | OG/2008 | JL/2008 | JU/2008 | MA/2008 | AP/2008 | Station |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 18-221 | 18 | 19 | 42 | 57 | 54 | 87 | 47 | 42 | 107 | 180 | 221 | 1 |
| 0-44 | 27 | 11 | 27 | 27 | 0 | 13 | 31 | 22 | 44 | 26 | 18 | 2 |
| 17-110 | 23 | 26 | 38 | 110 | 43 | 17 | 52 | 37 | 177 | 64 | 93 | 3 |
| 83-13 | 17 | 19 | 20 | 32 | 26 | 15 | 69 | 76 | 83 | 13 | 14 | 4 |
| 100-10 | 12 | 10 | 26 | 98 | 38 | 40 | 43 | 31 | 318 | 100 | 88 | 5 |
| 104-9 | 22 | 19 | 25 | 9 | 17 | 24 | 28 | 16 | 104 | 70 | 94 | 6 |

These plants were not have complete precipitating units and not controlled chlorination so water was could not suited for drinking because drinking water should be free from any microbial contamination(Mark &Hummer,2004).

]Statistical analysis

The statistical analysis of results by using correlation factor explain that some parameters are related with other parameters but not all as well as show bellow  in table 4.

Table 4 correlation factor among  parameters

| Bacteria | SO4-2 | Ca+2 | TH | Cl-1 | Alkalinity | EC | pH | parameter |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| - | 0.015 | - | - | - | - | - | 1 | pH |
| - | 0.001 | 0.002 | - | 0.025 | - | 1 | - | EC |
| - | - | 0.001 | 0.0 | - | 1 | - | - | Alkalinity |
| 0.0 | - | - | 0.009 | 1 | - | 0.025 | - | Cl-1 |
| - | - | 0.003 | 1 | 0.029 | 0.0 | - | - | TH |
| - | - | 1 | 0.003 | - | 0.001 | 0.002 | - | Ca+2 |
| - | 1 | - | - | - | - | 0.001 | 0.015 | SO4-2 |
| 1 | - | - | - | 0.0 | - | - | - | Bacteria |

References

Al-Azawey, Atheer Saieb.(2004).Study of some physical and chemical and bacterial pollution in water supply of Jurf alsakher in Babylon Governorate-Iraq, , M.SC. thesis, Babylon university.

Al-Azawi,Ebttsam Habeeb.(1998).Bacteria contamination of drinking water in Babylon province, M.SC. thesis, Babylon university.

Al-Mofraji,Talib.K.and Shatha S. Al-Azawi.(1991).Soil and water microbiology ,laboratory manual, Baghdad.

- APHA .(1975).  Standard methods for the examination of water and Waste  water, Sewage and industrials Wastes, ApHA. 7th  Edition.

Ashok G.(1998).Drinking water in developing countries, Anu. Rev. Energy environment , no(23):86-253.

Davison, S. (1999).Principles and practice of medicine , 18th edition ,UK, P464.

EPA.(1999).Drinking water and health ,EPA office water 4606 ,EPA861-k99.

Iraqi Standards .(1976). Water Quality Standards, C.O.S.Q.C, Iraq, MQA 417.

Mark, J. Hammer.(2004).water and wastewater technology,4th edition, printical Hall of India ,p,157.

Michalski.R. .(2005).Inorganic oxyhaide by products in drinking water and ion chromatographic determination method ,journal of environmental studies , vol 14 (3):227-268.

NHMRC .(2004).Australian drinking water  guidelines ,national water quality management strategy ,vol 6.

Nitm; Rc.(2004).National water quality management strategy ,Australian drinking water guideline.

Office of environmental health and safety.(2005).Nitrogen reducing technologies for onsite wastewater treatment system ,Olympia WA 98504-7825.

Onteria.(2006).Technical support document for drinking water standers objective and guide lines ,pibs,4449e01.

- Parsons; T. R., Maita; Y. and C. M. Lalli.(1984). Amanual of Chemical biological method for Sea water analysis, 1st Edition, Pergamon Press, Oxford.

- Taj-Aldeen ,Sawsan Samir Hadi.(2003).The study of water hardness in Al  Hilla river &how treat it for industrial uses in the general state of textile industry, M.SC. thesis, Babylon university.

- WHO .(2000). Berlin, Report of Drinking Water Quality Committee meeting, Geneva.

- WHO .(1996). Guidelines for drinking water quality, 2nd Edition, Geneva,, Vol.2, Health criteria of other supporting information, PP: 351-356.

WHO .(2004).Guideline for drinking water quality , Geneva 3ed edition ,vol 1.

- WHO.( 2000). Determination of Hardness of water, WHO method, m/26. Rl.

WHO.(2006).Guideline for drinking water quality,3ed edition,vol:1.