Effect of Unbalance Voltage on the Operation and Performance of a Three Phase Distribution Transformers

Mohammed k. Edan

Abstract-

Three phase supply system is found to be quite balanced in both magnitude and displacement at the generation levels but it is not so at distribution end. Voltage unbalance which is a common and global phenomenon is found to be very effective in deteriorating the operation and performance of electrical apparatus. Present paper is an attempt to analyze   the operation of three phase distribution transformers with unbalance voltage conditions.  MATLAB programming based upon symmetrical component approach is adopted to estimate the performance of a three-phase transformer under unbalanced condition. Both under voltage unbalance as well as over voltage unbalance have been considered for analysis purpose. Numerical details study in case of distribution transformer with primary delta connection and secondary star connection with solidly grounded neutral is presented in this paper.  The degree of voltage unbalance is represented by the voltage unbalance factor (VUF) derived from symmetrical component.

Key words: Transformer, Abnormal operation, symmetrical components, Voltage unbalance factor

الخلاصة

نظام تجهيز القدرة ثلاثي الطور يكون متزن القيمة و الزاوية  عند التوليد ولكن قد لايكون كذلك عند التوزيع . عدم اتزان الفولتية من الظواهر الشائعة التي تؤثر على تدهور عمل و اداء المعدات الكهربائيه . يقدم هّذا البحث محاولة لتحليل عمل محولات التوزيع ثلاثية الطور في حالة عدم اتزان الفولتية. تم انشاء برنامج باستخدام لغة البرمجة Matlab بالاعتماد على المركبات المتماثلة لتخمين اداء عمل المحولات ثلاثية الطور في حالة عدم الاتزان. حالة عدم اتزان الفولتية الناتج عن ارتفاع الفولتية وكذلك انخفاض الفولتية كلاهما تمت دراسة تأثيره.  قدم البحث دراسة عددية موسعة لمحولة ثلاثية الطور مؤرضة تأريضا مباشرا . استخدم عامل عدم اتزان الفولتية المشتق من المركبات المتماثلة لبيان مقدار عدم اتزان الفولتية.

1. Introduction

Voltage unbalance is the deviation of individual phase voltage magnitudes from the normal/rated values, with the individual phase voltages being not equal to each other either in magnitude and/or in phase displacement. The presence of inequality among the phase voltages can be attributed to the unsymmetrical impedances of transmission and distribution lines, unbalanced or unstable power utilities, unbalanced three phase loads, open delta transformer connections, blown fuses of a three-phase capacitor banks, uneven spread of single-phase loads across the three phases, single-phase traction loads, weak rural power electric systems with long transmission lines, or even unidentified/ uncleared single-phase-to-ground faults [ Giridhar Kini, Ramesh C. Bansal, and R. S. Aithal 2007].  Voltage unbalance can affect customer equipment, in particular, three phase induction motors can suffer from temperature rise due to the currents in the windings resulting from negative sequence voltage. Reduced torque and lower full-load speed can also result from voltage unbalance, possible resulting in the motor not being able to adequately fulfill its function. Other affects are an increase in noise and vibration [Neil Browne, Darren Spoor, and Justin Byrnes 2008]. Voltage unbalance can also affect performance of the network. It can result in increased voltage drop on conductors, resulting in the need for larger conductors. It can cause different losses on each phase of transformers, resulting in a rise in hot spot temperature. Unbalance can increase the generation of triplen harmonics, possibly overloading harmonic filters and capacitor banks [Z. Emin and D. Crisford 2006]. In the most practical studies, the method of measuring the voltage unbalanced level is either the percent voltage unbalance (PVU) defined by the (National Electrical Manufactures Association) NEMA or the voltage unbalance factor (VUF) defined by the (International Electrotechnical Commission) IEC. Both of them are positive real quantities which can show the level of voltage unbalance. The PVU is a method calculated by the sampled data of the ratio of the maximum deviation of the average voltage to the average of the three voltages. As for the VUF, it is described by the ratio of the negative sequence to the positive sequence voltage [Guilin Zheng and Yan Xu 2010].

2. Types of Voltage Unbalance

There may be different type of unbalance in a supply system and exists definite possibility of voltage variations above and below the rated value. Thus voltage unbalance can be classified into overvoltage unbalance (OVU) under-voltage unbalance (UVU) unbalance. OVU is a condition when the three phase voltages are not equal to each other, in addition positive sequence component is greater than the rated value while UVU is a condition where the three phase voltages are not equal to each other, and in addition the positive-sequence component is lesser than the rated value. There are many possible voltage unbalance in a power system, here we will study the following six causes, (1) single phase under voltage unbalance (1Φ-UV), (2) two phases under voltage unbalance (2Φ-UV), (3) three phases under voltage unbalance (3Φ-UV), (4) single phase over voltage unbalance (1Φ-OV), (5) two phases over voltage unbalance (2Φ-OV), (6) three phases over voltage unbalance (3Φ-OV) [Knwararjit Singh Sandhu and Vinnet Chaudhary 2009].

3. Unbalance in Three-Phase Distribution Networks

To study the unbalanced operation of a power system, the symmetrical components theory is used. According to Stokvis-Fortescue theorem, every three-phase asymmetrical system of phasors can be decomposed into three symmetrical systems of positive, negative and zero sequence respectively. Every sequence system contains three phasors characterized by equal magnitudes; in the case of positive and negative sequences, components are rotated between them with 120 electrical degrees in counter-clockwise direction and negative clockwise direction, respectively. In the case of zero sequence components, there is no rotation between phasors [ Chindriş, A. Cziker, Anca Miron, H.Bălan,and A. Sudria 2007]. If an asymmetrical system of line voltages is taken into consideration, the relationship between the initial system and the symmetrical sequence systems can be written as follows [E. Seiphetlho and A. P. J. Rens 2010]:

(1)

Where

Va, Vb and Vc are the unbalanced phase voltage Phasors   Vp, Vn and V0 the positive, negative and zero-sequence voltage phasors respectively (fundamental frequency components).

In the same way, if an asymmetrical system of line currents is taken into consideration, the relationship between the initial system and the symmetrical sequence systems can be written as follows [E. Seiphetlho and A. P. J. Rens 2010]:

(2)

Where

Ia, Ib and Ic are the unbalanced phase current Phasors Ip, In and I0 the positive, negative and zero-sequence currents phasors respectively (fundamental frequency components).

Where

= - 0.5+ j 0.866

These sequence systems are not only theoretical, they correspond to the reality: the positive sequence components are created by the synchronous or asynchronous generators while the negative and zero sequence components appear at the place of unbalance. Each of them can be separately measured and influence in a different way in power systems. For example, in the case of motors, the positive sequence components produce the useful torque while the negative sequence components produce fields that create braking torques. On other hand, the zero sequence components is the one that get involved in the cases of interferences between the electric and the telecommunication transmission lines [M. Chindriş, A. Cziker, Anca Miron, H.Bălan, and A. Sudria 2007].

4. Unbalance Definition

The two general definitions for voltage unbalance as described are;

4.1 NEMA Definition

The voltage unbalance percentage (VUP) at the terminal of a machine as given by the National Electrical Manufacturer Association Motor and Generator Standard (NEMA MGI) used in most studies is[K.S. Sandhu and Vineet Chaudhary 2008, P.Pillay and M.Manyage 2001]:

(3)

4.2 Symmetrical Component Definition

The voltage unbalance factor (VUF) is defined by International Electro technical Commission (IEC) as the ratio of negative-sequence voltage component to the positive-sequence voltage component [P.Pillay and M.Manyage 2001, J. M. Apsley 2010].

(4)

Where Vn and Vp are the magnitude of negative and positive sequence voltage components respectively are obtained by symmetrical component transformation.

5. Transformer Modeling Under Unbalance Condition

Steady state analysis of a transformer operating with unbalanced voltage is possible using symmetrical component approach. This requires the development of positive- , negative- and zero sequence equivalent circuit representation. It possible to assume for a transformer that X1 =X2 = leakage impedance. As the transformer is a static device, the positive or negative sequence impedances do not change with phase sequence of the applied balanced voltages. The zero sequence impedance can, however, vary from an open circuit to a low value depending on the transformer winding connection, method of neutral grounding [J. C. Das 2002].

The positive and negative sequence equivalent circuit representation of any transformer connection is shown in Fig.1 and Fig.2 respectively.

The zero sequence equivalent representation of transformer is dependent on the type of transformer winding connection .The zero sequence representation for a delta-star transformer with the star neutral solidly grounded is constructed as shown in Fig. 3(a).  The grounding of the star neutral allows the zero sequence currents to return through the neutral and circulate in the windings to the source of unbalance. On the delta side, the circuit is open, as no zero sequence currents appear in the lines, though these currents circulate in the delta windings to balance the ampere turns in the star windings. The circuit is open on the delta side line, and the zero sequence impedance of the transformer seen from the delta side is an open circuit [J. C. Das 2002]. If the star winding neutral is left isolated, Fig.3 (b), the circuit will be open on both sides, presenting infinite impedance [John J. Winders and Jr 2002].

In a star – star transformer connection, with both neutrals isolated, no zero sequence currents can flow. The zero sequence equivalent circuit is open on both sides and presents infinite impedance to the flow of zero sequence currents [John J. Winders, Jr, A. C. Franklin, and D. P. Franklin 1983].

For delta–delta connection, no zero currents will pass from one winding to another. On the transformer side, the windings are shown connected to the reference bus, allowing the circulation of currents within the windings [A. C. Franklin and D. P. Franklin 1983].

In star–star connected transformer, with both neutrals grounded the zero sequence equivalent circuit representation shown in Fig.4 [John J. Winders and Jr 2002, A. C. Franklin, and D. P. Franklin 1983].

Where per phase values are defined as:

Vpp    positive-sequence voltage

Vnp    negative-sequence voltage

V0s    zero-sequence voltage

RTp    primary resistance

XTp    primary reactance

RTs    secondary resistance referred to primary

XTs    secondary reactance referred to primary

Xm   magnetizing reactance

Zp      positive-sequence impedance of transformer

Zn    negative-sequence impedance of transformer

Z0    zero-sequence impedance of transformer

Ipp    primary positive-sequence current phasor

Ips    secondary positive-sequence current phasor

Inp    primary negative-sequence current phasor

Ins    secondary negative-sequence current phasor

I0p    primary positive-sequence current phasor

I0s    secondary positive-sequence current phasor

Let Vas , Vbs , and Vcs be the phase secondary voltages of a delta-star transformer with the star neutral soldely grounded . The corresponding zero-, positive and negative-sequence components (V0s ,Vps   and Vns) of the voltages are given by equation[E. Seiphetlho  and A. P. J. Rens 2010] :

(5)

The corresponding zero-, positive and negative-sequence components (I0s ,Ips   and Ins) of the currents are given by equation[M. Chindriş, A. Cziker, Anca Miron, H.Bălan, and A. Sudria 2007]:

(6)

Analysis of equivalent circuits the positive and negative primary phase voltages and currents can be determined from equations [Knwararjit Singh Sandhu, Vinnet Chaudhary 2009, A. C. Franklin, D. P. Franklin 1983]:

Vpp=(Vps×n×(ZLP+ZTs×(Zm+ZTp+ZTp×Zm))((ZLP×Zm))		(7)

Vnp=(Vns×n×(ZLn+ZTs×(Zm+ZTp+ZTp×Zm))((ZLn×Zm))		(8)

(9)

(10)

Where n is the transformer voltage ratio. The values of n are dependent on transformer connection as shown in Table 1 where Np  represents the primary turn number while Ns  has the same meaning for the secondary winding [M. Chindriş, A. Cziker, Anca Miron, H.Bălan, and A. Sudria 2007].

The primary is delta connected. The primary phase voltages and currents can be calculated by as [K.S. Sandhu and Vineet Chaudhary 2008]:

Vpa=Vpp+VnpVpb=a2∗Vpp+a2∗VnpVpc=a∗Vpp+a2∗Vnp                                                                     (11)

(12)

The transformer input, output power and primary and secondary power factor can be expressed in terms of symmetrical components of the voltage and currents as [E. Seiphetlho and A. P. J. Rens 2010]:

Input active power:

]                                  (13)

Input reactive power:

]                                      (14)

Where (*) indicates the conjugate value.

Primary power factor:

p.f=cos [tan−1(QinPin)]                                    		                 (15)

Output active power:

]                                (16)

Output reactive power:

]                   (17)

Secondary power factor:

p.f=cos [tan−1(QotPot)]						(18)

Total losses in watts:

Total losses = Pin- Pot 							(19)

Efficiency of the transformer is defined as:

(20)

6. System under study

To facilitate the analysis of unbalance and to understand the effect of unbalance voltage on  operation of distribution transformer, a system content of three phase  distribution transformer with delta primary winding connected and  star secondary winding with solidly grounding neutral. The transformer is loading with unbalance impedances as shown in figure (5).

The transformer and load have the following parameters:

- rated primary voltage Vp =11 Kv, rated secondary voltage Vs=415 V, transformer turn ratio N=45.9, transformer rated power ST= 250 KVA.

-  Primary impedance ZTp = (17.4 + j 40.3) Ω, secondary impedance reffered to primary ZTs = (13.4 + j 40.3) Ω.

- Load impedance reffered to primary   ZLa = (1310 + j 950) Ω,   ZLb = (1010 + j 650) Ω, ZLc = (1080 + j 450) Ω.

All parameters are on per phase basis

7. Results and Discussion

To study the effects of voltage unbalance on performance of distribution transformer, three causes of unbalancing the secondary voltage included under and over voltage are applied on the system under study.

Case 1: effect of three phase voltage unbalance.

(a)  Over voltage unbalance. It can be seen from table 2 that both efficiency and secondary power factor increase with increasing of unbalance factor.

(b)  Under voltage unbalance .It is observed from the results listed in table 2 that at under voltage unbalance in secondary voltage. The secondary power factor and transformer efficiency are decreased with increase of unbalance factor (VUF).

It also can be observed from table 3 for under and over voltage cases that the change in VUF is little effect on primary power factor.

The efficiency and total losses at over and under three phase voltage unbalance are 3-D plotted with unbalance factor in figures 6 and 8. The secondary and primary power factors are 3-D plotted with VUF in figures 7 and 9.

Case 2: effect of single phase voltage unbalance.

(a)  Over voltage unbalance.

For over voltage unbalance occurs in phase a. It can be seen from the results listed in table 4 that the secondary power factor and transformer efficiency decrease with increasing of VUF.

For over voltage unbalance occurs in phase b the transformer efficiency increases with increasing of VUF, while the secondary power factor decreases with increasing of VUF as shown in table 6.

For under voltage unbalance occurs in phase c the transformer efficiency and secondary power factor increase with increasing of VUF, as shown in table 8.

The efficiency and total losses for single phase over voltage unbalance occurs in phase    b is 3-D plotted with VUF in figure 10.The secondary and primary power factor is 3-D plotted with VUF in figure11.

(b)  Under voltage unbalance

For under voltage unbalance occurs in phase a. It can be seen from the results listed in tables 4 that the power factor and efficiency increase with increasing of VUF.

For under voltage unbalance occurs in phase b. The transformer efficiency decreases with increasing of VUF until VUF value 6.4518% and return to increases with increasing o VUF as shown in table 6.The secondary power factor increases with increasing of VUF as shown in table 6.

For under voltage unbalance occurs in phase c. The transformer efficiency and secondary power factor decreases with increasing of VUF, as shown in table 8.

The efficiency and total losses for single phase under voltage unbalance occurs in phase b is 3-D plotted with VUF in figure 12.The secondary and primary power factor is 3-D plotted with VUF in figure 13.

Case 3: effect of two phase voltage unbalance.

For unbalance voltage occurs in phase a and c.   It can be seen from the results listed in table 10 that the secondary positive – sequence voltage is fixed at VSP =239.0064 volt with different VUF values. It also can be observed that the efficiency and power factor decrease with increase of VUF. The maximum changes in efficiency and secondary power factor are 2.843% and 0.92% respectively.

The efficiency and total losses are 3-D plotted with VUF in figure 14.The secondary and primary power factor is 3-D plotted with VUF in figure 15.

For unbalance voltage occurs in phase a and b. It can be seen from result listed in table 12 that the positive – sequence voltage of the secondary voltage is fixed at the same above value. It also can be seen from results in table 10 that the efficiency and power factor decrease with increase of VUF. The maximum changes in efficiency and secondary power factor are 1.916% and 0.16% respectively. The efficiency and total losses are 3-D plotted with VUF in figure 16. The secondary and primary power factor is 3-D plotted with VUF in figures 17.

It can be seen from tables 10, 12 that the negative sequence voltage component has little effect on the power factor. In other word the transformer power factor affected by the positive sequence voltage component.

8. Conclusion

This paper presents analysis and control the operation of three-phase distribution transformer operating with unbalanced condition.

From the results of this paper it can be concluded the following:

1- The operating characteristics of a three phase distribution transformer will not be as good as in the balance case, but most customers do not know that the unbalance may cause a higher power factor. It is worth that customers usually use capacitors to improve the power factor, but due to ignorance of voltage unbalance, they may over compensate the power factor, thus result in over voltage.

2- The negative sequence voltage component has little effect on the secondary power factor.

3-The values of efficiency and secondary power factor dependent on over or under voltage unbalance for three phase unbalance. For two and single phase voltage unbalance the values of efficiency and secondary power factor  dependent on same reason of the three phase unbalance ,further dependent on  at which phase or phases the unbalance voltage occurs.

4-The voltage unbalance may causes decrease of transformer efficiency and increase transformer losses.

9. References

A. C. Franklin and D. P. Franklin, 1983, The J & P Transformer Book, Butterworth.

E. Seiphetlho and A. P. J. Rens, 2010, ” On the Assessment of Voltage Unbalance”, Proceeding of 14th International Conference on Harmonics and Quality of Power, page 1-6.IEEE Publisher.

Guilin Zheng and Yan Xu, 16-20 August 2010,  ” An Intelligent Three-Phase Voltage Unbalance Measuring Instrument Based on the ATT7022C”, Proceedings of the 2010 IEEE International Conference on Automation and Logistics, , Hong Kong and Macau.

J. C. Das, 2002, Power System Analysis Short-Circuit Load Flow and Harmonics, Marcel Dekker, Inc.

J. M. Apsley, 2 March-April 2010, “De-rating of multiphase induction machines due to supply unbalance”, IEEE Transaction on Industry Application, Volume 46, Issue.

John  J. Winders and Jr, 2002, Power Transformers Principles and Applications, Marcel Dekker, Inc.

Knwararjit Singh Sandhu and Vinnet Chaudhary, February 2009, ” Steady State Modelling of  Induction Motor Operating With Unbalanced Supply System”, Wseas Transaction on Circuit and Systems, Issue 2, Volume 8 .

K.S. Sandhu and Vineet Chaudhary, December 2008,” MATLAB & PSIM Based Analysis of Three- Phase Induction Motor Operation with Unbalanced Supply System”, Electrical Conference paper.

M. Chindriş, A. Cziker, Anca Miron, H.Bălan, and A. Sudria, 9-11 October 2007, ” Propagation of Unbalance in Electric Power Systems”,9th International Conference Power Quality and Utilisation. Barchelona.

Neil Browne, Darren Spoor, and Justin Byrnes, 2008, “Voltage Unbalance in an Urban Distribution Network - A Case Study”, 13th International Conference on Harmonics and Quality of Power, page 1-6.IEEE Publisher.

P. Giridhar Kini, Ramesh C. Bansal, and R. S. Aithal, August 2007, ” A Novel Approach Toward Interpretation and Application of Voltage Unbalance Factor “, IEEE Transaction on Industrial Electronics, Vol.54, No.4.

Z. Emin and D. Crisford, July 2006, “Negative phase sequence voltages on e and w transmission system,” IEEE Trans. Power Delivery., vol. 21, no. 3, pp. 1607– 1612.

P.Pillay and M.Manyage,”Definition of Voltage Unbalance, May 2001,” IEEE Power Engineering Review, vol.21, No.5, pp 49-51.

Table (1) Transformer ratio dependent on its connection

| Connection | n | Connection | n |
| --- | --- | --- | --- |
| Yy |  | Dy |  |
| Yd |  | Dd |  |
| Yz |  | Dz |  |

Table (2) results of transformer secondary circuit for 3 –phases under and over voltage unbalance

|  | VUF% | Vas | Vbs | Vcs | Ias | Ibs | Ics | Vsp | Vsn | Vso | PF | Total losses Watts | Efficiency % |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 0.0000 | 239.6004 | 239.6004 | 239.6004 | 312.0781 | 420.4602 | 431.6304 | 239.6004 | 0.0000 | 0.0000 | 0.8672 | 21795 | 91.6972 |
| U V U | 1.5604 | 237.5169 | 231.2664 | 225.0160 | 309.3644 | 405.8355 | 405.3573 | 231.2664 | 3.6087 | 3.6087 | 0.8652 | 22026 | 90.9961 |
|  | 3.2375 | 235.4334 | 222.9325 | 210.4316 | 306.6507 | 391.2108 | 379.0841 | 222.9325 | 7.2174 | 7.2174 | 0.8630 | 22103 | 90.2853 |
|  | 5.0448 | 233.3499 | 214.5986 | 195.8473 | 303.9370 | 376.5861 | 352.8109 | 214.5986 | 10.8261 | 10.8261 | 0.8606 | 22028 | 89.5691 |
|  | 6.9982 | 231.2664 | 206.2647 | 181.2629 | 301.2232 | 361.9614 | 326.5378 | 206.2647 | 14.4348 | 14.4348 | 0.8580 | 21801 | 88.8550 |
|  | 9.1161 | 229.1830 | 197.9307 | 166.6785 | 298.5095 | 347.3367 | 300.2646 | 197.9307 | 18.0435 | 18.0435 | 0.8552 | 21422 | 88.1526 |
| O V U | 1.4555 | 241.6838 | 247.9343 | 254.1847 | 314.7918 | 435.0849 | 457.9036 | 247.9343 | 3.6087 | 3.6087 | 0.8691 | 21413 | 92.3839 |
|  | 2.6962 | 244.8091 | 256.2682 | 268.7691 | 318.8624 | 449.7097 | 484.1767 | 256.6155 | 6.9188 | 6.9188 | 0.8708 | 21134 | 92.9871 |
|  | 3.9731 | 246.8925 | 264.6021 | 283.3535 | 321.5761 | 464.3344 | 510.4499 | 264.9494 | 10.5268 | 10.5268 | 0.8724 | 20457 | 93.6381 |
|  | 5.1723 | 248.9760 | 272.9361 | 297.9378 | 324.2899 | 478.9591 | 536.7230 | 273.2833 | 14.1351 | 14.1351 | 0.8739 | 19628 | 94.2696 |
|  | 6.3006 | 251.0595 | 281.2700 | 312.5222 | 327.0036 | 493.5838 | 562.9962 | 281.6172 | 17.7436 | 17.7436 | 0.8752 | 18647 | 94.8810 |
|  | 7.3641 | 253.1430 | 289.6039 | 327.1066 | 329.7173 | 508.2085 | 589.2693 | 289.9512 | 21.3522 | 21.3522 | 0.8765 | 17513 | 95.4720 |
|  | 8.4786 | 254.1847 | 297.9378 | 341.6910 | 331.0742 | 522.8332 | 615.5425 | 297.9378 | 25.2609 | 25.2609 | 0.8778 | 15917 | 96.1100 |

Table (3) results of transformer primary circuit for 3 –phases under and over voltage unbalance

|  | VUF% | Vap | Vbp | Vcp | Iap | Ibp | Icp | Vpp | Vpn | PF |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 0.0000 | 11655 | 11655 | 11655 | 9.1735 | 9.1735 | 9.1735 | 11655 | 0.0000 | 0.8184 |
| U V U | 1.5604 | 11402 | 11251 | 11098 | 8.9649 | 8.8792 | 8.7208 | 11250 | 175.5455 | 0.8184 |
|  | 3.2174 | 11146 | 10854 | 10542 | 8.7541 | 8.5898 | 8.2691 | 10845 | 348.9089 | 0.8185 |
|  | 5.0135 | 10893 | 10458 | 9986 | 8.5459 | 8.3018 | 7.8174 | 10439 | 523.3634 | 0.8186 |
|  | 6.9547 | 10640 | 10065 | 9432 | 8.3389 | 8.0166 | 7.3661 | 10034 | 697.8179 | 0.8189 |
|  | 9.0594 | 10389 | 9677 | 8879 | 8.1331 | 7.7346 | 6.9153 | 09628 | 872.2723 | 0.8192 |
| O V U | 1.4465 | 11911 | 12060 | 12213 | 9.3846 | 9.4686 | 9.6261 | 12061 | 174.5 | 0.8184 |
|  | 2.6794 | 12201 | 12476 | 12780 | 9.6232 | 9.7740 | 10.0833 | 12483 | 334.5 | 0.8185 |
|  | 3.9484 | 12458 | 12885 | 13338 | 9.8359 | 10.0726 | 10.5363 | 12888 | 508.9 | 0.8185 |
|  | 5.1402 | 12715 | 13296 | 13897 | 10.0494 | 10.3729 | 10.9894 | 13294 | 683.3 | 0.8186 |
|  | 6.2615 | 12973 | 13709 | 14457 | 10.2636 | 10.6746 | 11.4427 | 13699 | 857.8 | 0.8188 |
|  | 7.3183 | 13231 | 14123 | 15016 | 10.4784 | 10.9777 | 11.8961 | 14105 | 1032.2 | 0.8189 |
|  | 8.4259 | 13457 | 14532 | 15569 | 10.6673 | 11.2746 | 12.3454 | 14493 | 1221.2 | 0.8191 |

Table (4) results of transformer secondary circuit for 1 –phase under and over voltage unbalance in phase a

|  | VUF% | Vas | Vbs | Vcs | Ias | Ibs | Ics | Vsp | Vsn | Vso | PF | Total losses Watts | Efficiency% |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 0.0000 | 239.6004 | 239.6004 | 239.6004 | 312.0781 | 420.4602 | 431.6304 | 239.6004 | 0.0000 | 0.0000 | 0.8672 | 21795 | 91.6972 |
| U V U | 2.0710 | 225.0160 | 239.6004 | 239.6004 | 293.0821 | 420.4602 | 431.6304 | 234.7389 | 4.8615 | 4.8615 | 0.8690 | 18519 | 92.6537 |
|  | 4.2296 | 210.4316 | 239.6004 | 239.6004 | 274.0860 | 420.4602 | 431.6304 | 229.8774 | 9.7229 | 9.7229 | 0.8707 | 15250 | 93.7014 |
|  | 6.4815 | 195.8473 | 239.6004 | 239.6004 | 255.0899 | 420.4602 | 431.6304 | 225.0160 | 14.5844 | 14.5844 | 0.8724 | 11994 | 94.8440 |
|  | 8.8328 | 181.2629 | 239.6004 | 239.6004 | 236.0939 | 420.4602 | 431.6304 | 220.1545 | 19.4458 | 19.4458 | 0.8740 | 8748 | 96.0873 |
|  | 11.2903 | 166.6785 | 239.6004 | 239.6004 | 217.0978 | 420.4602 | 431.6304 | 215.2931 | 24.3073 | 24.3073 | 0.8756 | 5512 | 97.4359 |
| O V U | 1.9886 | 254.1847 | 239.6004 | 239.6004 | 331.0742 | 420.4602 | 431.6304 | 244.4618 | 4.8615 | 4.8615 | 0.8655 | 25084 | 90.8248 |
|  | 3.8997 | 268.7691 | 239.6004 | 239.6004 | 350.0702 | 420.4602 | 431.6304 | 249.3233 | 9.7229 | 9.7229 | 0.8638 | 28383 | 90.0315 |
|  | 5.7377 | 283.3535 | 239.6004 | 239.6004 | 369.0663 | 420.4602 | 431.6304 | 254.1847 | 14.5844 | 14.5844 | 0.8621 | 31693 | 89.3120 |
|  | 7.5067 | 297.9378 | 239.6004 | 239.6004 | 388.0624 | 420.4602 | 431.6304 | 259.0462 | 19.4458 | 19.4458 | 0.8604 | 35014 | 88.6609 |
|  | 9.2105 | 312.5222 | 239.6004 | 239.6004 | 407.0584 | 420.4602 | 431.6304 | 263.9076 | 24.3073 | 24.3073 | 0.8587 | 38345 | 88.0733 |
|  | 10.8527 | 327.1066 | 239.6004 | 239.6004 | 426.0545 | 420.4602 | 431.6304 | 268.7691 | 29.1687 | 29.1687 | 0.8571 | 41687 | 87.5444 |
|  | 12.4365 | 341.6910 | 239.6004 | 239.6004 | 445.0505 | 420.4602 | 431.6304 | 273.6306 | 34.0302 | 34.0302 | 0.8555 | 45040 | 87.0695 |

Table (5) results of transformer primary circuit for 1 –phase under and over voltage unbalance in phase a

|  | VUF% | Vap | Vbp | Vcp | Iap | Ibp | Icp | Vpp | Vpn | PF |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 0.0000 | 11655 | 11655 | 11655 | 9.1735 | 9.1735 | 9.1735 | 11655 | 0.0000 | 0.8184 |
| U V U | 2.0710 | 11182 | 11539 | 11539 | 8.7978 | 9.0564 | 9.1109 | 11419 | 236.5 | 0.8184 |
|  | 4.2033 | 10712 | 11420 | 11429 | 8.4253 | 8.9382 | 9.0523 | 11182 | 470 | 0.8186 |
|  | 6.4412 | 10241 | 11309 | 11321 | 8.0515 | 8.8263 | 8.9953 | 10946 | 705 | 0.8188 |
|  | 8.7779 | 9769 | 11201 | 11217 | 7.6778 | 8.7182 | 8.9408 | 10709 | 940.1 | 0.8191 |
|  | 11.2202 | 9298 | 11097 | 11117 | 7.3043 | 8.6143 | 8.8888 | 10473 | 1175.1 | 0.8196 |
| O V U | 1.9763 | 12127 | 11778 | 11774 | 9.5477 | 9.2964 | 9.1735 | 11892 | 235 | 0.8184 |
|  | 3.8755 | 12598 | 11905 | 11896 | 9.9221 | 9.4228 | 9.2376 | 12128 | 470 | 0.8185 |
|  | 5.7020 | 13070 | 12035 | 12021 | 10.2966 | 9.5524 | 9.3039 | 12365 | 705 | 0.8187 |
|  | 7.4600 | 13541 | 12168 | 12150 | 10.6712 | 9.6851 | 9.3725 | 12601 | 940.1 | 0.8189 |
|  | 9.1533 | 14013 | 12304 | 12281 | 11.0458 | 9.8208 | 9.4433 | 12838 | 1175.1 | 0.8192 |
|  | 10.7853 | 14484 | 12443 | 12416 | 11.4205 | 9.9594 | 9.5162 | 13074 | 1410.1 | 0.8195 |
|  | 12.3593 | 14956 | 12585 | 12553 | 11.7953 | 10.1007 | 9.5912 | 13311 | 1645.1 | 0.8199 |

Table (6) results of transformer secondary circuit for 1 –phase under and over voltage unbalance in phase b

|  | VUF% | Vas | Vbs | Vcs | Ias | Ibs | Ics | Vsp | Vsn | Vso | PF | Total losses Watts | Efficiency % |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 0.0000 | 239.6004 | 239.6004 | 239.6004 | 312.0781 | 420.4602 | 431.6304 | 239.6004 | 0.0000 | 0.0000 | 0.8672 | 21795 | 91.6972 |
| U V U | 2.0710 | 239.6004 | 225.0160 | 239.6004 | 312.0781 | 394.8670 | 431.6304 | 234.7389 | 4.8615 | 4.8615 | 0.8684 | 21373 | 91.5214 |
|  | 4.2296 | 239.6004 | 210.4316 | 239.6004 | 312.0781 | 369.2738 | 431.6304 | 229.8774 | 9.7229 | 9.7229 | 0.8695 | 20780 | 91.4176 |
|  | 6.4815 | 239.6004 | 195.8473 | 239.6004 | 312.0781 | 343.6805 | 431.6304 | 225.0160 | 14.5844 | 14.5844 | 0.8707 | 20019 | 91.3939 |
|  | 8.8328 | 239.6004 | 181.2629 | 239.6004 | 312.0781 | 318.0873 | 431.6304 | 220.1545 | 19.4458 | 19.4458 | 0.8718 | 19090 | 91.4613 |
|  | 11.2903 | 239.6004 | 166.6785 | 239.6004 | 312.0781 | 292.4941 | 431.6304 | 215.2931 | 24.3073 | 24.3073 | 0.8730 | 17992 | 92.5623 |
| O V U | 1.9886 | 239.6004 | 254.1847 | 239.6004 | 312.0781 | 446.0535 | 431.6304 | 244.4618 | 4.8615 | 4.8615 | 0.8661 | 22050 | 91.9344 |
|  | 3.8997 | 239.6004 | 268.7691 | 239.6004 | 312.0781 | 471.6467 | 431.6304 | 249.3233 | 9.7229 | 9.7229 | 0.8651 | 22137 | 92.2253 |
|  | 5.7377 | 239.6004 | 283.3535 | 239.6004 | 312.0781 | 497.2399 | 431.6304 | 254.1847 | 14.5844 | 14.5844 | 0.8640 | 22055 | 92.5623 |
|  | 7.5067 | 239.6004 | 297.9378 | 239.6004 | 312.0781 | 522.8332 | 431.6304 | 259.0462 | 19.4458 | 19.4458 | 0.8630 | 21804 | 92.9388 |
|  | 9.2105 | 239.6004 | 312.5222 | 239.6004 | 312.0781 | 548.4264 | 431.6304 | 263.9076 | 24.3073 | 24.3073 | 0.8621 | 21385 | 93.3485 |
|  | 10.8527 | 239.6004 | 327.1066 | 239.6004 | 312.0781 | 574.0196 | 431.6304 | 268.7691 | 29.1687 | 29.1687 | 0.8612 | 20798 | 93.7859 |
|  | 12.4365 | 239.6004 | 341.6910 | 239.6004 | 312.0781 | 599.6129 | 431.6304 | 273.6306 | 34.0302 | 34.0302 | 0.8603 | 20042 | 94.2463 |

Table (7) results of transformer primary circuit for 1 –phase under and over voltage unbalance in phase b

|  | VUF% | Vap | Vbp | Vcp | Iap | Ibp | Icp | Vpp | Vpn | PF |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 0.0000 | 11655 | 11655 | 11655 | 9.1735 | 9.1735 | 9.1735 | 11655 | 0.0000 | 0.8184 |
| U V U | 2.0710 | 11182 | 11539 | 11539 | 8.7978 | 9.0564 | 9.1109 | 11419 | 236.5 | 0.8184 |
|  | 4.2033 | 10712 | 11420 | 11429 | 8.4253 | 8.9382 | 9.0523 | 11182 | 470 | 0.8186 |
|  | 6.4412 | 10241 | 11309 | 11321 | 8.0515 | 8.8263 | 8.9953 | 10946 | 705 | 0.8188 |
|  | 8.7779 | 9769 | 11201 | 11217 | 7.6778 | 8.7182 | 8.9408 | 10709 | 940.1 | 0.8191 |
|  | 11.2202 | 9298 | 11097 | 11117 | 7.3043 | 8.6143 | 8.8888 | 10473 | 1175.1 | 0.8196 |
| O V U | 1.9763 | 12127 | 11778 | 11774 | 9.5477 | 9.2964 | 9.1735 | 11892 | 235 | 0.8184 |
|  | 3.8755 | 12598 | 11905 | 11896 | 9.9221 | 9.4228 | 9.2376 | 12128 | 470 | 0.8185 |
|  | 5.7020 | 13070 | 12035 | 12021 | 10.2966 | 9.5524 | 9.3039 | 12365 | 705 | 0.8187 |
|  | 7.4600 | 13541 | 12168 | 12150 | 10.6712 | 9.6851 | 9.3725 | 12601 | 940.1 | 0.8189 |
|  | 9.1533 | 14013 | 12304 | 12281 | 11.0458 | 9.8208 | 9.4433 | 12838 | 1175.1 | 0.8192 |
|  | 10.7853 | 14484 | 12443 | 12416 | 11.4205 | 9.9594 | 9.5162 | 13074 | 1410.1 | 0.8195 |
|  | 12.3593 | 14956 | 12585 | 12553 | 11.7953 | 10.1007 | 9.5912 | 13311 | 1645.1 | 0.8199 |

Table (8) results of transformer secondary circuit for 1 –phase under and over voltage unbalance in phase c

|  | VUF% | Vas | Vbs | Vcs | Ias | Ibs | Ics | Vsp | Vsn | Vso | PF | Total losses Watts | Efficiency % |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 0.0000 | 239.6004 | 239.6004 | 239.6004 | 312.0781 | 420.4602 | 431.6304 | 239.6004 | 0.0000 | 0.0000 | 0.8672 | 21795 | 91.6972 |
| U V U | 2.0710 | 239.6004 | 239.6004 | 225.0160 | 312.0781 | 420.4602 | 405.3573 | 234.7389 | 4.8615 | 4.8615 | 0.8643 | 22642 | 91.0181 |
|  | 4.2296 | 239.6004 | 239.6004 | 210.4316 | 312.0781 | 420.4602 | 379.0841 | 229.8774 | 9.7229 | 9.7229 | 0.8613 | 23237 | 90.4025 |
|  | 6.4815 | 239.6004 | 239.6004 | 195.8473 | 312.0781 | 420.4602 | 352.8109 | 225.0160 | 14.5844 | 14.5844 | 0.8583 | 23586 | 89.8604 |
|  | 8.8328 | 239.6004 | 239.6004 | 181.2629 | 312.0781 | 420.4602 | 326.5378 | 220.1545 | 19.4458 | 19.4458 | 0.8551 | 23687 | 89.4052 |
|  | 11.2903 | 239.6004 | 239.6004 | 166.6785 | 312.0781 | 420.4602 | 300.2646 | 215.2931 | 24.3073 | 24.3073 | 0.8519 | 23539 | 89.0507 |
| O V U | 1.9886 | 239.6004 | 239.6004 | 254.1847 | 312.0781 | 420.4602 | 457.9036 | 244.4618 | 4.8615 | 4.8615 | 0.8700 | 20702 | 92.4276 |
|  | 3.8997 | 239.6004 | 239.6004 | 268.7691 | 312.0781 | 420.4602 | 484.1767 | 249.3233 | 9.7229 | 9.7229 | 0.8727 | 19361 | 93.2004 |
|  | 5.7377 | 239.6004 | 239.6004 | 283.3535 | 312.0781 | 420.4602 | 510.4499 | 254.1847 | 14.5844 | 14.5844 | 0.8752 | 17771 | 94.0070 |
|  | 7.5067 | 239.6004 | 239.6004 | 297.9378 | 312.0781 | 420.4602 | 536.7230 | 259.0462 | 19.4458 | 19.4458 | 0.8777 | 15933 | 94.8401 |
|  | 9.2105 | 239.6004 | 239.6004 | 312.5222 | 312.0781 | 420.4602 | 562.9962 | 263.9076 | 24.3073 | 24.3073 | 0.8800 | 13847 | 95.6931 |
|  | 10.8527 | 239.6004 | 239.6004 | 327.1066 | 312.0781 | 420.4602 | 589.2693 | 268.7691 | 29.1687 | 29.1687 | 0.8821 | 11513 | 96.5600 |
|  | 12.4365 | 239.6004 | 239.6004 | 341.6910 | 312.0781 | 420.4602 | 615.5425 | 273.6306 | 34.0302 | 34.0302 | 0.8842 | 8931 | 97.4361 |

Table (9) results of transformer primary circuit for 1 –phase under and over voltage unbalance in phase c

|  | VUF% | Vap | Vbp | Vcp | Iap | Ibp | Icp | Vpp | Vpn | PF |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 0.0000 | 11655 | 11655 | 11655 | 9.1735 | 9.1735 | 9.1735 | 11655 | 0.0000 | 0.8184 |
| U V U | 2.0710 | 11539 | 11539 | 11182 | 9.0564 | 9.1109 | 8.7978 | 11419 | 236.5 | 0.8184 |
|  | 4.2033 | 11420 | 11429 | 10712 | 8.9382 | 9.0523 | 8.4253 | 11182 | 470 | 0.8186 |
|  | 6.4412 | 11309 | 11321 | 10241 | 8.8263 | 8.9953 | 8.0515 | 10946 | 705 | 0.8188 |
|  | 8.7779 | 11201 | 11217 | 9769 | 8.7182 | 8.9408 | 7.6778 | 10709 | 940.1 | 0.8191 |
|  | 11.2202 | 11097 | 11117 | 9298 | 8.6143 | 8.8888 | 7.3043 | 10473 | 1175.1 | 0.8196 |
| O V U | 1.9763 | 11778 | 11774 | 12127 | 9.2964 | 9.2376 | 9.5477 | 11892 | 235 | 0.8184 |
|  | 3.8755 | 11905 | 11896 | 12598 | 9.4228 | 9.3039 | 9.9221 | 12128 | 470 | 0.8185 |
|  | 5.7020 | 12035 | 12021 | 13070 | 9.5524 | 9.3725 | 10.2966 | 12365 | 705 | 0.8187 |
|  | 7.4600 | 12168 | 12150 | 13541 | 9.6851 | 9.4433 | 10.6712 | 12601 | 940.1 | 0.8189 |
|  | 9.1533 | 12304 | 12281 | 14013 | 9.8208 | 9.5162 | 11.0458 | 12838 | 1175.1 | 0.8192 |
|  | 10.7853 | 12443 | 12416 | 14484 | 9.9594 | 9.5912 | 11.4205 | 13074 | 1410.1 | 0.8195 |
|  | 12.3593 | 12585 | 12553 | 14956 | 10.1007 | 9.6683 | 11.7953 | 13311 | 1645.1 | 0.8199 |

Table (10) results of transformer secondary circuit for 2 –phases voltage unbalance in phase a and c

| VUF% | Vas | Vbs | Vcs | Ias | Ibs | Ics | Vsp | Vsn | Vso | PF | Total losses Watts | Efficiency% |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0.0000 | 239.6004 | 239.6004 | 239.6004 | 312.0781 | 420.4602 | 431.6304 | 239.6004 | 0.0000 | 0.0000 | 0.8672 | 21795 | 91.6972 |
| 1.0001 | 243.7509 | 239.6004 | 235.4498 | 317.4842 | 420.4602 | 424.1534 | 239.6004 | 2.3963 | 2.3963 | 0.8659 | 22988 | 91.2437 |
| 2.0003 | 247.9015 | 239.6004 | 231.2992 | 322.8903 | 420.4602 | 416.6763 | 239.6004 | 4.7927 | 4.7927 | 0.8646 | 24147 | 90.8056 |
| 3.0004 | 252.0520 | 239.6004 | 227.1487 | 328.2964 | 420.4602 | 409.1992 | 239.6004 | 7.1890 | 7.1890 | 0.8633 | 25271 | 90.3831 |
| 4.0005 | 256.2026 | 239.6004 | 222.9981 | 333.7024 | 420.4602 | 401.7222 | 239.6004 | 9.5853 | 9.5853 | 0.8620 | 26360 | 89.9765 |
| 5.0007 | 260.3531 | 239.6004 | 218.8476 | 339.1085 | 420.4602 | 394.2451 | 239.6004 | 11.9816 | 11.9816 | 0.8606 | 27414 | 89.5859 |
| 6.0008 | 264.5037 | 239.6004 | 214.6970 | 344.5146 | 420.4602 | 386.7680 | 239.6004 | 14.3780 | 14.3780 | 0.8593 | 28435 | 89.2117 |
| 7.0009 | 268.6543 | 239.6004 | 210.5465 | 349.9207 | 420.4602 | 379.2910 | 239.6004 | 16.7743 | 16.7743 | 0.8580 | 29420 | 88.8540 |

Table (11) results of transformer primary circuit for 2 –phases voltage unbalance in phase a and c

| VUF% | Vap | Vbp | Vcp | Iap | Ibp | Icp | Vpp | Vpn | PF |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0.0000 | 11655 | 11655 | 11655 | 9.1735 | 9.1735 | 9.1735 | 11655 | 0.0000 | 0.8184 |
| 0.9939 | 11755 | 11657 | 11555 | 9.2457 | 9.1905 | 9.0849 | 11655 | 115.8451 | 0.8184 |
| 1.9878 | 11855 | 11660 | 11454 | 9.3183 | 9.2085 | 8.9965 | 11655 | 231.6902 | 0.8184 |
| 2.9818 | 11956 | 11664 | 11354 | 9.3912 | 9.2274 | 8.9082 | 11655 | 347.5353 | 0.8185 |
| 3.9757 | 12057 | 11670 | 11254 | 9.4646 | 9.2473 | 8.8201 | 11655 | 463.3804 | 0.8185 |
| 4.9696 | 12157 | 11676 | 11154 | 9.5383 | 9.2680 | 8.7320 | 11655 | 579.2255 | 0.8186 |
| 5.9635 | 12259 | 11683 | 11055 | 9.6124 | 9.2897 | 8.6441 | 11655 | 695.0706 | 0.8187 |
| 6.9574 | 12360 | 11692 | 10956 | 9.6868 | 9.3122 | 8.5563 | 11655 | 810.9157 | 0.8189 |

Table (12) results of transformer secondary circuit for 2 –phases voltage unbalance in phase a and b

| VUF% | Vas | Vbs | Vcs | Ias | Ibs | Ics | Vsp | Vsn | Vso | PF | Total lossesWatts | Efficiency% |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0.0000 | 239.6004 | 239.6004 | 239.6004 | 312.0781 | 420.4602 | 431.6304 | 239.6004 | 0.0000 | 0.0000 | 0.8672 | 21795 | 91.6972 |
| 1.0001 | 243.7509 | 235.4498 | 239.6004 | 317.4842 | 413.1767 | 431.6304 | 239.6004 | 2.3963 | 2.3963 | 0.8671 | 22619 | 91.3844 |
| 2.0003 | 247.9015 | 231.2992 | 239.6004 | 322.8903 | 405.8931 | 431.6304 | 239.6004 | 4.7927 | 4.7927 | 0.8669 | 23415 | 91.0843 |
| 3.0004 | 252.0520 | 227.1487 | 239.6004 | 328.2964 | 398.6096 | 431.6304 | 239.6004 | 7.1890 | 7.1890 | 0.8666 | 24182 | 90.7972 |
| 4.0005 | 256.2026 | 222.9981 | 239.6004 | 333.7024 | 391.3260 | 431.6304 | 239.6004 | 9.5853 | 9.5853 | 0.8664 | 24922 | 90.5233 |
| 5.0007 | 260.3531 | 218.8476 | 239.6004 | 339.1085 | 384.0424 | 431.6304 | 239.6004 | 11.9816 | 11.9816 | 0.8662 | 25633 | 90.2626 |
| 6.0008 | 264.5037 | 214.6970 | 239.6004 | 344.5146 | 376.7589 | 431.6304 | 239.6004 | 14.3780 | 14.3780 | 0.8659 | 26316 | 90.0154 |
| 7.0009 | 268.6543 | 210.5465 | 239.6004 | 349.9207 | 369.4753 | 431.6304 | 239.6004 | 16.7743 | 16.7743 | 0.8656 | 26972 | 89.7817 |

Table (13) results of transformer secondary circuit for 2 –phases voltage unbalance in phase a and b

| VUF% | Vap | Vbp | Vcp | Iap | Ibp | Icp | Vpp | Vpn | PF |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0.0000 | 11655 | 11655 | 11655 | 9.1735 | 9.1735 | 9.1735 | 11655 | 0.0000 | 0.8184 |
| 0.9939 | 11755 | 11657 | 11555 | 9.2457 | 9.1905 | 9.0849 | 11655 | 115.8451 | 0.8184 |
| 1.9878 | 11855 | 11660 | 11454 | 9.3183 | 9.2085 | 8.9965 | 11655 | 231.6902 | 0.8184 |
| 2.9818 | 11956 | 11664 | 11354 | 9.3912 | 9.2274 | 8.9082 | 11655 | 347.5353 | 0.8185 |
| 3.9757 | 12057 | 11670 | 11254 | 9.4646 | 9.2473 | 8.8201 | 11655 | 463.3804 | 0.8185 |
| 4.9696 | 12157 | 11676 | 11154 | 9.5383 | 9.2680 | 8.7320 | 11655 | 579.2255 | 0.8186 |
| 5.9635 | 12259 | 11683 | 11055 | 9.6124 | 9.2897 | 8.6441 | 11655 | 695.0706 | 0.8187 |
| 6.9574 | 12360 | 11692 | 10956 | 9.6868 | 9.3122 | 8.5563 | 11655 | 810.9157 | 0.8189 |

jXTs

RTs

jXTp

RTp

I0p=0

No

I0s=0

Z0

V0s

+

-

-

+

jXTs

Rc

RTs

jXTp

RTp

Ipp

-

+

ZP

Vpp

Ips

Ipm

jXm

Vps

Fig.1 Per-phase positive sequence representation

-

+

jXTs

Rc

RTs

jXTp

RTp

Inp

-

+

Zn

Vnp

Ins

Inm

jXm

Vns

(b)

Fig.3 (a) Derivations of equivalent zero sequence circuit for a delta–star transformer, star neutral solidly grounded; (b) zero sequence circuit of a delta–star transformer, star neutral isolated.

Fig.2 Per-phase negative sequence representation

IO

IO

0

IO

0

0

Primary

Secondary

jXTs

Rc

RTs

jXTp

RTp

I0p

-

+

Z0

V0p

I0s

Ipm

jXm

V0s

jXTs

RTs

jXTp

RTp

I0p=0

No

I0s

Z0

V0s

+

-

Fig.4 Per-phase zero sequence representation of a wye–wye transformer, both neutrals grounded.

(a)

Zbc

Zab

Zc

Za

Zb

ZLc

ZLb

ZLa

Vab

Zac

ICP

Ibp

Iap

Ias

c

Ics

Ibc

a

b

Primary

Secondary

Vac

Vbc

0

0

0

0

0

0

Primary

Secondary

Fig.5 system under study

Fig.6. 3-D plot of VUF, total losses and efficiency for 3-phases over voltage unbalance

Fig.9. 3-D plot of VUF, secondary and primary power factor for 3-phases under voltage unbalance

Fig.7. 3-D plot of VUF, secondary and primary power factor for 3-phases over voltage unbalance

Fig.10. 3-D plot of VUF, total losses and efficiency for 1-phase over voltage unbalance in phase b

Fig.8. 3-D plot of VUF, total losses and efficiency for 3-phases under voltage unbalance

Fig.11. 3-D plot of VUF, secondary and primary power factor for 1-phase over voltage unbalance in phase b

Fig.12. 3-D plot of VUF, total losses and efficiency for 1-phase under voltage unbalance in phase b

Fig.15. 3-D plot of VUF, secondary and primary power factor for 2-phase voltage unbalance in phase a and c

Fig.13. 3-D plot of VUF, secondary and primary power factor for 1-phase under voltage unbalance in phase b

Fig.16. 3-D plot of VUF, total losses and efficiency for 2-phases voltage unbalance in phase a and b

Fig.14. 3-D plot of VUF, total losses and efficiency for 2-phases voltage unbalance in phase a and c

Fig.17. 3-D plot of VUF, secondary and primary power factor for 2-phases voltage unbalance in phase a and b