Theoretical Study For The Effect Of Different Fuels On The Perfomance Of Open Gas Turbine Power Plant

Mohamed F. Thabit Al-dawoodi

Department of mechanical engineering, Al-Qadissiya University, Al-Qadissiya, Iraq

Abstract

The use of gas turbine is increasing day by day for producing electricity and for various industrial applications.  It’s well-known that thermal efficiency of open gas turbine varies with the fuel used in the combustion process. In this work an investigation for the effect of different hydrocarbon, alcohol and hydrogen fuels on the performance of simple and modified gas turbine has been studied. A computer program was written in Quick basic Language has been accomplished to calculate the thermal efficiency, work ratio, specific fuel consumption….etc. in gas turbine working with different types of fuels. It’s found that specific fuel consumption is margined according to the fuel used because its dependency on the enthalpy of reaction of the fuel. Also it’s noted that hydrogen fuel has higher thermal efficiency and lower fuel consumption than other fuels, but its requires high pressure to insert it to combustor. Therefore we must use methane as fuel in the plant since it is more common type than other.

الخلاصة

يتزايد انتشار التوربين الغازي يوما بعد يوم في توليد الطاقة الكهربائية وفروع الصناعة الأخرى. من المعروف ان الكفاءة الحرارية لدورة التوربين الغازي المفتوحة تتغير حسب نوع الوقود المستخدم في المحطة. تم في هذا البحث دراسة تاثير انواع مختلفة من الوقود على كفاءة وأداء دورة التوربين الغازي البسيطة والمطورة.  حيث تم إعداد برنامج بلغة بيسك لحساب الكفاءة الحرارية ومعدل استهلاك الوقود ونسبة الشغل المنجز للتوربين الغازي  الذي يعمل على انواع مختلفة من الوقود مثل الهايدروكاربونات بالإضافة الى الوقود الهايدروجيني كذلك تم دراسة تاثير نسبة الضغط ودرجة الحرارة العظمى على اداء المحطة. كما لوحظ إن نوع الوقود المستخدم يحدد كمية الاستهلاك النوعي له وذلك نتيجة لاعتماده على مقدار المحتوى الحراري لذلك الوقود.فقد تم التوصل الى ان الوقود الهايدروجيني  يمتلك اعلى كفاءة مع اقل استهلاك  نوعي ياتي بعده سائل الميثان والبروبين والبنزين ثم المجموعة الكحولية, لكن الهايدروجين يتطلب ضغط عالي لادخاله الى غرفة الاحتراق, لذا يجب استخدام الميثان كوقود بديلا عن الهايدروجين لكونه اكثر الانواع شيوعا واستخداما

Nomenclature

| Symbol | Definition | Unit |
| --- | --- | --- |
| T | Temperature | K |
| Cp | Specific Heat at Constant Pressure | kJ/kg.K |
| C1,C2 | Parameters of Fuels | - |
| h | Specific Enthalpy | kJ/kg |
| f | Fuel to Air Ratio | - |
| W | Work | kJ/kg |
| S.F.C. | Specific Fuel Consumption | Kg/kW.hr |
| PR | Pressure Ratio | - |

Greek Symbols

| Symbol | Definition | Unit |
| --- | --- | --- |
| γ | Specific Heat Ratio |  |
| η | Efficiency |  |
| ΔH | Enthalpy of Reaction per unit Mass | kJ/kg |

Subscript

| Symbol | Definition |
| --- | --- |
| a | Air |
| b | Burner |
| c | Compressor |
| g | Gas |
| m | Mechanical |
| max. | Maximum |
| n | Net |
| r | Ratio |
| t | Turbine |

Introduction

The wide use of electrical energy is one of the most important characters of each century and its large consumption considered and a feature of highly developed countries. Most of the governments and companies to complete the production of electrical energy and its distribution to help users employ it for different purposes: domestic, industrial and commercial.  Although the thermal efficiency of closed gas turbine cycles was independent of the fuel used in the combustion process. (leung E., 1985) presented in his paper an investigation about the performance of open gas turbine. The principle result of his study was a correlation between the variation of the thermal efficiency with both hydrocarbon fuel and alcohol, and the fuel parameter C1+C2 taken from the equation of reaction. Practical and theoretical study of performance of simple gas turbine cycle for power generation performed by (Badran, 1997), for two power stations “Rehab and Rasha stations” at different load. The result showed that an increase in compressor inlet temperature yields to decrease in the efficiency & an increase in turbine inlet temperature causes increased in the work which in turn increase in thermal efficiency and decreased in the fuel consumption. Also when pressure ratio increased, the thermal efficiency increased up to a maximu8m value and then started decreased indicating that there is an optimum pressure ratio for a given value of turbine inlet temperature. (Rice, 1987)  studies in his investigation a heat balance method of evaluating various open gas turbine cycle systems based on the first law of thermodynamics. A useful solution is presented that can be applied to various gas turbine configurations. (Lefebvre, 1985) presented in his paper an analytical study for the effect of fuel properties on the performance and reliability of several gas turbine combustors. Its concluded that combustion efficiency depend on fuel chemistry, but are strongly influenced by the physical fuel properties that govern atomization quality and spray evaporation rates. (Foster, 1990) studies an efficient, indirectly heated steam injected air turbine power fired with coal. The plant meet all environmental standards and generate about 35 kW. The plant offers high power without requiring condensing steam turbine and can operate efficiently. (Schefer, 2002) has studied the combustion process of hydrogen when blended with traditional hydrocarbon fuels in gas turbine combustors. The objectives of his work are:

1. effect of the amount of hydrogen on flame stability, combustor acoustics, emissions and efficiency.

2. Establish a scientific and technological database for lean combustion of hydrogen-enriched fuels.

3. Establish the numerical simulation capabilities that will facilitate design optimization of lean premixed swirl burner. The approach was used to design and fabricate a lean premixed swirl burner that simulate the basic features of gas turbine combustors The results of study showed that ultra-lean premixed combustion is an effective approach to NOx emissions reduction from gas turbine engines. Hydrogen blended with traditional hydrocarbon fuels significantly improves flame stability during lean combustion and allows stable combustion at low temperature needed to minimize NOx production.

Hydrogen, as a carbon-free energy carrier, is likely to play an important role in a world with serve constraints on gas emissions. In the power industry, its utilization as gas turbine fuel can be proposed under several possible scenarios, depending on the mode of H2 production (Chiesa, P, 2005). For instance, hydrogen can be produced remotely from renewable energy sources (solar and wind) or from nuclear energy (via direct thermal conversion or by electrolysis!), but in a more realistic and near-term vision it will be derived from conventional fossil fuels by conversion process including CO2 sequestration. Possible solutions include: (i) remote coal conversion to hydrogen (via gasification, shift, and separation from CO2 and H2 pipeline transport to the power station, (ii) integrated hydrogen and electricity production from coal or natural gas, exporting pure hydrogen to remote users on-side low- grade hydrogen to produce power (Kreutz, T. G. et al,2002), (iii) electrical generation from combined cycles integrated to fossil fuel decarburization ( applicable to coal, oil, or gas and CO2) capture (Lozza, G., and Chiesa, P.,2002), Fuel cells and H2-O2 semi closed cycles may represent future options for power generation, but combined cycles coupled to H2 production/ CO2 sequestration processes can be proposed as a short/mid-term solution for massive gas emission reduction

Theoretical Analysis

In this work the mathematical analysis falls into two sections, the first section deals with the analysis of simple cycle of open gas turbine, and the second section deals with the analysis of modified cycle open gas turbine which include (intercooling, reheat, and heat exchanger). All theoretical analysis of this study are made under the following assumptions:

1.Both compression and expansion processes are isentropic.

2.No Kinetic energy change between inlet and outlet of each component.

3. The pressure drop through air inlet, combustion chamber, Nozzles…etc, are neglected.

4. Mass flow rate is constant through the cycle.

Simulation Of Simple Cycle

Fig.(1) show a simplified diagram of simple gas turbine which describes all components of the plant

1. Compressor: This part represented in process 1-2 of Figure (1) where the task of compressor  is increase the pressure of incoming air so that the compression and power extraction processes after combustion can be carried out more efficiently. During the isentropic compression process:

T2T1=P2P1γa−1γa=PRγa−1γa

(1)

The isentropic efficiency of compressor is defined as the ratio of work input required in isentropic compression between P1& P2  to the actual work required, (Willard W,1997).

ηc=T2−T1T2−T1                                                                                                                                           (2)

So the work input to the compressor is:

Wc=Cpa∗T2−T1ηm            ; where  ηm mechanical efficiency                                                        (3)

2. Combustion Chamber: This part is represented in process 2--3 of (T-S) diagram. In Figure (2). The combustion chamber is designed to burn a mixture of fuel and air to deliver the resulting gases to the turbine at a uniform temperature. The gas temperature of the turbine must not exceed the allowable structure temperature of the turbine (Jack, D.1998) .A schematic of combustion chamber is shown in Figure (3). Since the process is adiabatic with no work transfer, so the energy equation, (Cohen, 1989)  is simply ;

mihi,3−h2−f.hf,t=0                                                                		(4)

Now making the enthalpy of reaction at a reference temperature of 25 oc, so equation can be expanded in the usual way (Cohen, 1989)  to get;

1+ft.Cpg.T3−298+ft.ΔH25+Cpa.298−T2+ft.Cpf298−Tf=0             (5)

By simplifying equation (5) the theoretical fuel to air ratio will be:

ft=Cpg.T1−T3+Cpa.T2−T1Cpg.T3−T1+ΛH25                                                                            (6)

The actual (fuel / air) ratio for given temperature difference is given by;

fa=ftηb

(7)

3. Turbine: The purpose of turbine is to extract kinetic energy from the expanding gases which flow from the combustion chamber (Jack, D.1998). The kinetic energy is converted to shaft horse power to drive the compressor and other components. Nearly three-forth of all energy available from the product of combustion is required to drive the compressor. This part is represented in process 3-4- of (T-S) diagram In Figure (2).

During the isentropic expansion process (Easjop T.D.,1978):

T4T3=P4P3γg−1γg=PRγg−1γg

(8)

Similarly the isentropic efficiency of compressor is defined as the ratio of actual work output to the isentropic work output between P3 and P4

ηt=T3−T4T3−T4

(9)

Then the turbine work output is:

Wt=Cpg∗T3−T4                                                                                             (10)

The net work output is determine by subtracting equation (10) from equation (3). The work ratio is defined as the ratio of net work output to turbine output work (Easjop T.D.,1978):.

WR=WnWt                                                                                                          (11)

The specific fuel consumption is given by;

S.F.C.=fa×3600Wn

(12)

Then the cycle thermal efficiency is found there from the equation below (Jack, D.1998);

ηth=3600S.F.C.∗ΔH25                                                                                                (13)

The following Correlation was obtained to get maximum thermal efficiency (leung E., 1985)

ηmax=25.47+29.2∗J+2.2+3.3∗J.lnC1+C2%      where J=lnTmax1000             (14)

The above equation examined the variation of maximum thermal efficiency with both hydrocarbon and alcohol fuels with fuel parameter C1+C2 taken from the equation of reaction:

Cfuel+O2→C1CO2+C2H2O                                                                (15)

Simulation Of Modified Cycle

Possible modification to the basic cycle can be made (Cohen, 1989), such as Intercooling (use more compressor), reheating (use more combustor), and heat exchanger which uses some of the energy in the turbine exhaust gases to preheat the air entering the compressor. In this work we should summarized these modification as follows:

1. Intercooling: When the compression process is performed in two stages with an intercooler, then the work input for a given pressure ratio and mass flow is reduced. The task of intercooler is to reduce the outlet temperature of low pressure compressor which is equal to the temperature inlet to high pressure compressor at the same pressure. The system of intercooling and (T-S) diagram are shown in Figure (4) and Figure (5) respectively. To get the work input is a minimum, we must make the pressure in each stage of compression is the same, when the temperature of air is cooled in the intercooler, back to the inlet to the unit (plant)  So:

T3=T1     (16)

During the isentropic processes (1-2-)  & (3-4-)

P2P1=P4P3	  (17)

T2T1=P2P1γa−1γa=PRγa−1γa        &       T4T3=P4P3γa−1γa=PRγa−1γa                              (18)

The isentropic efficiencies of low and high pressure compressors is given below:

ηc1=T2−T1T2−T1      &     ηc2=T4−T3T4−T3                                                               (19)

The total work of compressors is calculated from the equation;

Wctot=Cpa∗T2−T1+T4−T3ηm (20)

2. Reheat: The expansion process is very frequently performed in two separate stages. The high pressure turbine driving the compressor and low pressure turbine providing the useful power output. The work output of the low pressure turbine can be increased by raising the temperature at the inlet of the stage. This can be done by placing a second combustion chamber between the turbine stages (Cohen, 1989), in order to heat the gases leaves the high pressure turbine. This system with the (T-S) diagram are shown in Figure.(6), and Figure (7). The high pressure turbine must be exactly equal to the work input for the compressor  with the following equation

Cpa.T2−T1ηm=Cpg.T3−T4	                                                                          (21)

For the first combustion chamber, the energy equation is used (Cohen, 1989)

mihi,3−h2−f.hft1=0                                                                            (22)

The first theoretical fuel/air ratio is calculated from expanding equation (22) as follows

1+ft1.Cpg.T3−298+ft1.ΔH25+Cpa.298−T2+ft1.Cpf298−Tf=0          (23)

The same procedure is used for second combustion chamber;

mihi,4−h4−f.hft2=0                   						 (24)

The second fuel/air ratio is then calculated as follows;

1+ft2.Cpg.T5−298+ft2.ΔH25+Cpg.298−T4+ft2.Cpf298−Tf=0     	     (25)

Then the total fuel/air ratio is given by;

ft,tot=ft1+ft2                  								(26)

The net work of the plant is equal to work output of low pressure turbine

Wn=Wt2=Cpg.T5−T6                                                                         		 (27)

3.Heat Exchanger: The exhaust gases leaving the turbine at the end of expansion are still at a high temperature (high enthalpy). If these gases are allowed to pass into atmosphere, this represent a loss of available energy, this energy can be recovered by passing the gases from the turbine through a heat exchanger, where the heat transfer from the gases is used to heat the air leaving the compressor. Therefore the function of heat exchanger is to heat the outlet air from compressor (T/2 to T3)  and to cooled the exhausted gases from turbine (T/5-T6) as shown in Figure.(8) and Figure (9), so the ideal heat exchanger have (T/2=T6) and (T3=T/5) which is assumed in this work.

The other performance parameters are repeated with the same procedure applied in simple cycle.

Results And Discussion

The layout of the results is divided into two sections, these explain the effect of maximum temperature and pressure ratio on the performance of simple and modified of open gas turbine plant respectively. In this work we studied different types of fuels which are (H2, CH4, C3H6 , C6H6, CH3OH) that are used in gas turbine cycle. Figure (10) shows the relation between maximum plant temperature with different types of fuels. Equation (14) is used to draw this plot. It can be seen that when maximum cycle increased, the maximum efficiency also increased. When we make comparison between the fuels used, it can be noted that hydrogen and methyl alcohol have the same higher maximum efficiency than other fuels at the same operating conditions, this is because they have greater fuel parameter (C1+C2), see table (1). Figure (11) shows the effect of maximum cycle temperature which was varied from (1100-2000) Ko on the thermal efficiency for all fuels considered. In general the thermal efficiency increases with increase in temperature of cycle. The hydrogen curve is on the top of the plot because it has higher enthalpy of reaction (lower calorific value) then methane…., with methyl alcohol which came last because it has lower energy than other fuels. Figure (12) represent the relation between maximum cycle temperature with the specific fuel consumption. It can be noted that hydrogen fuel has minimum specific fuel consumption than other fuels and this expected because hydrogen has higher thermal efficiency and according to equation (13) hydrogen fuel must has minimum specific fuel consumption followed by methane, propen, benzene, and finally methyl alcohol. Now the graphs of thermal efficiency and specific fuel consumption are repeated for all fuels selected, but for variable pressure ratio (4-9), and for fixed maximum temperature 1600 Ko, see Figure (13) and Figure (14). When pressure ratio is increased, the thermal efficiency increased for all fuels but hydrogen and methane fuels remain in the top of the plot. In the graphs of modify open gas turbine power plant which include (intercooling, reheat, and heat exchanger),   Only hydrogen and methane fuels is graphed, since methane fuel is the more common type used in gaseous plant, and hydrogen is promising fuel which have maximum efficiency, and minimum fuel consumption than other fuels. The use of hydrogen as a fuel appears to promise a significant improvement in performance of gaseous plants and reduces the emissions of Greenhouse gases, nitrogen oxide, and smoke. Another driving force behind the need to use hydrogen fuels is the rapid depletion rate of currently used fossil fuels. Figure (15) and Figure (16) shows the effect of maximum temperature and pressure ratio on the thermal efficiency and S.F.C. of intercooling cycle operating on hydrogen and methane fuels respectively. It can be noted from Figure (15) the thermal efficiency increase with increase in maximum temperature for a fixed pressure ratio (PR=4), this increase is greater than in simple cycle about 12 % . Also there is a reduction in S.F.C. bout 35% as compared with simple cycle this because increase in net work and thermal efficiency for both fuels selected. Figure (16) shows the effect of pressure ratio variation on the thermal efficiency and specific fuel consumption with maximum temperature equal to 1600 Ko.. Its observed that when pressure ratio increased, the thermal efficiency increased, until reaches to maximum value then starts to decrease indicating that there is an optimal pressure ratio equal 7 at which the maximum thermal efficiency is 0.360255 and specific fuel consumption is 0.08327 ( kg/kW.hr) for hydrogen fuel. The same behavior is observed for methane fuel when PR=7, thermal efficiency and S.F.C. are 0.3537 & .20557 (kg/kW.hr) respectively. Figure (17) and Figure (18) shows the effect of maximum temperature and pressure ratio on the thermal efficiency and S.F.C. of reheating cycle operating on hydrogen and methane fuels respectively.. In the reheating cycle the increase in thermal efficiency is lower than the increased in the intercooling cycle. Also there is a reduction in the S.F.C. about 17 % this is due to increase in the net work output and hence in the thermal efficiency. It can be seen from Figure (18) that thermal efficiency increased with increased in pressure ratio, also a reduction in S.F.C. is obtained. In the case of heat exchanger cycle the thermal efficiency is increased with increase in the maximum temperature reaches to 0.5233009 at 2000 Ko for a fixed pressure ratio equal to 4, but this behavior is opposite when pressure ratio varied and maximum temperature fixed to 1600 Ko. Its observed maximum efficiency equal to 0.4760761 at PR= 4 then starts to decrease when pressure ratio increased. This is clearly observed in Figure (19) and Figure (20) respectively. Figure (21) explain the effect of maximum temperature on the work ratio for simple and modified cycle of gas turbine power plant operated with hydrogen fuel. It can noted from this figure that maximum work ratio occurred with the intercooling cycle followed by reheating cycle, then simple and heat exchanger cycle which are have the same curve because the condition of the ideal heat exchanger haves (T/2=T6) and (T3=T/5) see Figure (8) which gives the same turbine work and hence gives the same  work ratio

Conclusion

The following conclusions can be drawn from the present work;

Hydrogen fuel is ideal promising fuel in the gaseous plant which has greater thermal efficiency, and hence minimum S.F.C. than other selected fuels. Greater improvement in the performance of modified gas turbine power plant occurred with intercooling and heat exchanger rather than simple and reheat cycle.

References

Badran O. “ Study in gas turbine performance improvements” ,Journal of Eng. Sciences Vol.4, No.2, 1997.

Chiesa, P., Lozza G., Mazzocchi, L."using hydrogen as gas turbine fuel", Journal of Eng. For gas turbine and power, Jan.,Vol. 127, 2005

Cohen H,Rogers ,“gas turbine theory”, john wily,1989.

Easjop T.D. ”Applied thermodynamics for Eng. Technology”, 1978.

Foster R.W. “A small air turbine power plant fired with coal in an atmospheric fluid bed” Journal of Eng. Science for gas turbine and power,  Jan. 1990.

Gulder O.L. “Combustion gas properties and prediction of partial pressures of CO2 & H2O in combustion gases of aiation and diesel fuels”, Journal of Eng. Science for gas turbine and power,  July, 1986.

Jack, D. Mattingly, "Element of gas Turbine", 1998.

Kreutz, T. G. et al., (Production of hydrogen and electricity from coal with CO2 capture," Proc. Of the sixth international conference on " Green gas control Technologies", Kyoto, Japan, 2002.

Lefebve A.H. “fuel effect on gas turbine combustion ignition stability and combustion efficiency”, Journal of Mechanical Eng., 1985.

Leung E.Y.W. “Universal Correlation for the thermal efficiency of open gas turbine by using different fuels”, Journal of Eng. Science for gas turbine and power, Vol.107, July, 1985.

Lozza G., Chiesa, P., " CO2 sequestration techniques for IGCC and natural gas power plants:" a comparative estimation of their thermodynamic and economic performance", Proc. Of the international conference on clean coal technologies (CCT 2002), Chia Laguna, Italy, 2002.

Schefer, R., "Reduced Turbine Emissions Using Hydrogen-Enriched Fuels" Progress report By Dep.of Energy, June, 2002, Web Site :< www.doe.com.>.

Willard W. “Engineering Fundamentals of I.C.E”. , 1997.

Saba Y.A. “Modeling and prediction the performance of Al-Hilla gas turbine power plant, M.Sc. Thesis, University of Babylon, 2000.

Table (1)  Fuels Input Data

| Type of fuel | Phase | Lower calorific value (kJ/kg) | C1+C2 |
| --- | --- | --- | --- |
| H2 | gas | 120000 | 2 |
| CH4 | liquid | 49500 | 1.5 |
| C3H6 | liquid | 45000 | 1.333 |
| C6H6 | liquid | 40000 | 1.20 |
| CH3OH | liquid | 19700 | 2 |

Table (2) operating conditions of the plant

| Compressor inlet temperature (T1) | 298 Ko |
| --- | --- |
| Specific heat ratio of air (γa) | 1.4 |
| Specific heat ratio of exhaust gas (γg) | 1.3333 |
| Pressure ratio (PR) | (4-9) |
| Isentropic efficiency of compressor (ηc) | 85 % |
| Isentropic efficiency of turbine (ηt) | 87 % |
| Mechanical efficiency | 98 % |
| Efficiency of burner | 98 % |
| Fuel temperature (Tf) | 298 |

Fig.(1) Simplified diagram of simple gas turbine                Fig.(2) (T-S) diagram of simple gas Power plant (Saba Y., 2000)                                                turbine cycle

Fig.(3) A schematic of combustion chamber in gas turbine power plant (Saba Y., 2000)

Fig.( 4) Simplified diagram of Intercooling gas turbine              Fig.(5) (T-S) diagram of Power plant                                                                                         intercooling cycle

Fig.( 6) Simplified diagram Reheating gas turbine       Fig.(7) (T-S) diagram of reheating cycle

Power plant

Fig.( 8) Simplified diagram heat exchanger gas turbine      Fig.(9) (T-S) diagram of heat

Power plant					exchanger cycle

Fig.(10) Effect of maximum cycle Temperature 	Fig.(11) Effect of maximum cycle Temperature

on the max. Efficiency for simple cycle                on the thermal Efficiency for simple cycle

Fig.(12) Effect of maximum cycle Temperature 	  Fig.(13) Effect of Pressure ratio on the thermal

on the S.F.C. for simple cycle                                          Efficiency for simple cycle

Fig.(14) Effect of Pressure ratio on the S.F.C.       Fig.(15) Effect of Max. Temperature on the            thermal for simple cycle                                     efficiency & S.F.C. for intercooling cycle

Fig.(16) Effect of Pressure ratio on the S.F.C.        Fig.(17) Effect of Max. Temperature on the thermal effi. for intercooling cycle                       thermal efficiency & S.F.C. for reheating cycle

Fig.(18) Effect of Pressure ratio on the S.F.C.        Fig.(19) Effect of Max. Temperature on the   thermal effi. for reheating cycle                     thermal efficiency & S.F.C. for heat exchanger cycle

Fig.(20) Effect of Pressure ratio on the S.F.C.                Fig.(21) Effect of Max. temperature on the work           &   efficiency for heat exchanger cycle                      ratio for simple and modify gas turbine cycle