A QUASI-STEADY STATE OPERATION MODE OF ALTERNATIVE REFRIGERANTS FOR R-22 IN WATER CHILLERS

Ali Hussain Tarrad               Fouad Alwan Saleh                Deyaa Mohammed N. Mahmood

Department of Mechanical Engineering, College of Engineering,

Al-Mustansiriya University, Baghdad,

ABSTRACT:

The zeotropic blends comprise of R-407C and R-404A refrigerants and the pure R-134a were selected as a drop-in substitutes for R-22 in a water chiller under a quasi-steady state operation. When comparing the performance of the refrigerants with those of R-22, the results showed that R-407C, R-404A and R-134a reduced the cooling capacity up to (6) %, (6-12) % and (18) % respectively. R-134a and R-407C exhibited higher power consumption per ton of refrigeration than that experienced with the R-22 tests by (8-28) % and (7) % respectively. Whereas, R-404A showed a lower corresponding value than that of the R-22 by (9) %. The R-407C and R-404A showed a significant reduction in the actual (COP) by (19-23) % and (22-55) % respectively. The (COP) of the R-134a showed oscillation when compared with R-22 ranging from (22) % lower at high water inlet temperature to (29) % higher at low water inlet temperature.

KEYWORDS: Refrigeration, Alternatives, Zeotrope, R-22, Chiller, Quasi-Steady

ألطور التشغيلي الشبه مستقر لبدائل التثليج لفريون R-22 لوحدات إنتاج الماء المثلج

الخلاصة

تم استخدام موائع التثليج المكونة من خلائط زيوتروبية والمؤلفة من R-407C و R-404A بالإضافة إلى المائع النقي R-134a  كبدائل لمائع التثليج R-22 في وحدة تبريد الماء لظروف تشغيلية شبه مستقرة من دون إجراء أي تحوير على منظومة التبريد. عند مقارنة النتائج فقد أبدت جميع البدائل نقصان لسعة التبريد تصل إلى (6) % للمائع R-407C و (6-12)% للمائع R-404A في حين كانت حوالي (18) % لمائع التثليج R-134a. المائعان R-134a و R-407C قد أبديا طاقة مستهلكة لكل طن تبريد بقيمة أعلى عند مقارنتها بتلك المستهلكة