EXPERIMENTAL STUDY OF AIR DISTRIBUTION

WITHIN  OPERATION ROOM

Dr. Adil A. Alwan                                                   Hasan F. Abd Ali

E-mail: adil_almoosway@yahoo.com

E-mail: hasan.ivf@gmail.com

University of Babylon, College of Engineering/ Mechanical Eng. Department.

P.O.Box  No. 4  Hilla-Iraq

Abstract  :-

The experimental analysis includes a patient  lying on an operation table, surgical staff members, and surgical lights above the patient.  The cold clean air is supplied to the room through grilles from ceiling diffusers and exhausted through low side walls. The first aim of the experimental study is to investigate the validity of air distribution within operation room and the effect of using the air filtering on the air flow distribution. Different air distribution system to what exists in the optical operation room, is also investigated by locating the inlet at the upper part of  a  side wall, while the exhaust grilles were in the lower part of the opposite side.  From this study, it was found that the temperature and relative humidity in the surgical zone are 21.3oC and 49.3% in the optical operation room. While, the values in the experimental operation room are 23.6oC and 45.3%.  These values in both operation rooms are in the acceptable range of the surgical conditions as well as for the carbon dioxide. Therefore, it can be using the wall air supply system in the operation room with good conditions for the surgical work.

Keywords: Air conditioning, Ventilation, Operation room, Experimental operation room, Filtration.

دراسة عملية لتوزيع الهواء خلال غرفة العمليات

د.عادل عباس علوان           حسن فليح عبد علي

جامعة بابل/ كلية الهندسة/ قسم الهندسة الميكانيكية

الخلاصة:

تضمن التحليل العملي  مريض يرقد على طاولة العمليات والفريق الجراحي حول المريض والمصابيح الجراحية فوق المريض.  تم تزويد الهواء النقي البارد للغرفة من خلال شبكات (grilles) من خلال ناشرات الهواء السقفية وثم طرد الهواء من أسفل الجداران. الهدف الأول من الدراسة العملية هو اختبار نظام توزيع الهواء من حيث درجة الحرارة والرطوبة النسبية و سرعة الهواء وذلك لمعرفة مدى صلاحية نظام توزيع الهواء المستخدم حاليا في غرف العمليات. كما تم دراسة تأثير عملية التنقية باستخدام فلتر على توزيع جريان الهواء داخل غرفة العمليات.  تم استخدام نظام توزيع هواء مغاير لما موجود في غرفة العمليات الواقعية وذلك بجعل نظام تجهيز الهواء من خلال ((diffuser في أعلى احد الجوانب أما منافذ السحب فقد كان في الجزء الأسفل من الجانب المقابل.  من هذه الدراسة, تم إيجاد أن درجة الحرارة والرطوبة النسبية في نطاق منطقة العمل الجراحي هي 21.2oC و  49.3%  في غرفة العمليات الواقعية.  بينما في غرفة العمليات التجريبية فأنها 23.6oC و 45.3% .  هذه القيم في كلتا غرفتي العمليات هي في المدى المقبول لشروط العمل الجراحي وكذلك بالنسبة لغاز ثنائي اوكسيد لكاربون. لذلك فانه من الممكن استخدام نظام تجهيز الهواء ألجداري في غرفة العمليات مع توفير شروط جيدة للعمل الجراحي.